APPROVED BY C.E.I.G., LICENSE NO: CEIG/TS/OTK NO.02/D.NO.229/2024 DT: 19-02-24 to 22-02-27

(As per IS: 6792-1972 with 2.5mm gap) TRANSFARMER OIL TEST CERTIFICATE

To,	SL NO: 082/2025

M/s. SILVER PRINTS PVT LTD,	DATE: 29-11-2025

93&94 A.P. APPAREL PARK, GUNDLAPOCHAMPALLY, MEDCHAL MDL, HYD-14.

| TRANSFORMER DETAILS | MAKE : ESENNAR | QTY OF OIL : 1160 Liters |
| --- | --- | --- |
|  | RATING: 630 KVA | MFG YEAR : 2017 |
|  | VOLTAGE RATIO: 11/0.433KV | SL NO OF TF : ET2-8009 |

- DIELECTRIC STRENGTH OF TRANSFORMER OIL: Before Filtration/After Filtration.

| SAMPLES | VOLTAGE APPLIED | TIME IN SECONDS | VOLTAGE APPLIED | TIME IN SECONDS | CONDITION OF THE OIL OK/ UNSATISFACTORY |
| --- | --- | --- | --- | --- | --- |
| BOTTOM I | 28KV | 60 | 60KV | 60 | OK |
| BOTTOM II | 29KV | 60 | 60KV | 60 | OK |
| TOP | 28KV | 60 | 65KV | 60 | OK |

NOTE: Testing Method as Per IS 6792-1992.

Min.BDV as per IS 1866:200 30kv at 60Sec is Considered to be good. If Less Than that oil should be filtered.

- INSULATION RESISTANCE OF WINDINGS IN MEGA OHMS:

| H.T SIDE |  |  | L.T SIDE |  |  | H.T To L.T |  |  | RESULTS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R.E | B.E | Y.E | R.E | B.E | Y.E | R.R | B.B | Y.Y |  |
| 1600 | 1600 | 1600 | 1500 | 1500 | 1500 | 1600 | 1600 | 1600 | OK |

- ACIDITY OF TRANSFORMER OIL

| 0.03 milligram of KOH per gram of oil | Result : | OK |  | UNSATISFACTORY |  |
| --- | --- | --- | --- | --- | --- |